## Size
Component | Unit | Total
PV panels | kW | 235.04
Wind turbines | kW | 0
Battery bank | kWh | 296.63
Diesel Genset | kW | 38.17

## Cost
Cost item | Component | Scenario | Unit | Total
Net present cost | System | - | kUSD | 987.281
Total Investment cost | System | - | kUSD | 537.122
Total fixed O&M cost | System | - | kUSD | 78.139
Total variable O&M cost | System | - | kUSD | 464.011
Salvage value | System | - | kUSD | -91.991
Levelized Cost of Energy | System | - | USD/kWh | 0.2946
Investment cost | PV panels | - | kUSD | 470.074
| Wind turbines | - | kUSD | 0.001
| Battery bank | - | kUSD | 56.36
| Diesel Genset | - | kUSD | 10.687
Fixed cost | PV panels | - | kUSD | 25.996
| Wind turbines | - | kUSD | 0
| Battery bank | - | kUSD | 8.454
| Diesel Genset | - | kUSD | 0.197
Lost load cost | System | 1 | kUSD | 22.116
Replacement cost | Battery bank | 1 | kUSD | 1.392
Fuel cost | Diesel | 1 | kUSD | 440.504

## Yearly cash flows
| Fixed costs |  |  |  | Lost load cost | Replacement cost | Fuel cost
Component | PV panels | Wind turbines | Battery bank | Diesel Genset | System | Battery bank | Diesel
Scenario | - | - | - | - | 1 | 1 | 1
Unit | kUSD | kUSD | kUSD | kUSD | kUSD | kUSD | kUSD
Year 1 | 4.23 | 0 | 8.45 | 0.03 | 3.6 | 0.23 | 71.62
Year 2 | 4.23 | 0 | 8.45 | 0.03 | 3.6 | 0.23 | 71.7
Year 3 | 4.23 | 0 | 8.45 | 0.03 | 3.6 | 0.23 | 71.7
Year 4 | 4.23 | 0 | 8.45 | 0.03 | 3.6 | 0.23 | 71.7
Year 5 | 4.23 | 0 | 8.45 | 0.03 | 3.6 | 0.23 | 71.7
Year 6 | 4.23 | 0 | 8.45 | 0.03 | 3.6 | 0.23 | 71.7
Year 7 | 4.23 | 0 | 8.45 | 0.03 | 3.6 | 0.23 | 71.7
Year 8 | 4.23 | 0 | 8.45 | 0.03 | 3.6 | 0.23 | 71.7
Year 9 | 4.23 | 0 | 8.45 | 0.03 | 3.6 | 0.23 | 71.7
Year 10 | 4.23 | 0 | 8.45 | 0.03 | 3.6 | 0.23 | 71.7

## Yearly energy parameters
| Generators share | Renewables penetration | Curtailment share | Battery usage
| % | % | % | %
Year 1 | 34.83 | 66.23 | 7.44 | 12.23
Year 2 | 34.87 | 66.2 | 7.42 | 12.2
Year 3 | 34.87 | 66.2 | 7.42 | 12.2
Year 4 | 34.87 | 66.2 | 7.42 | 12.2
Year 5 | 34.87 | 66.2 | 7.42 | 12.21
Year 6 | 34.87 | 66.2 | 7.42 | 12.21
Year 7 | 34.87 | 66.2 | 7.42 | 12.21
Year 8 | 34.87 | 66.2 | 7.42 | 12.21
Year 9 | 34.87 | 66.2 | 7.42 | 12.21
Year 10 | 34.87 | 66.2 | 7.42 | 12.21